## Start
© Eaton Corporation
Revision 0.0
1. Press 'Enter Thermal Data' Button and answer questions regarding enclosure size, expected ambient temperature enclosure color, etc.

## Details
Heat Transfer Calculator Details | [6 empty] | Step:
Enclosure Dimensions | [6 empty] | 1. Enter required data into white fields.
Height (in) | 70 | inches |  |  |  |  | either manually, or press the button here:
Width (in) | 42 | inches |  |  |  |  | 2. Calculated A/C size is shown in yellow field.
Depth (in) | 20 | inches |  |  |  |  | 3. Make sure you check or uncheck the "Allow reflections"
Calculated Area (ft2) | 66.1111 | square ft. |  |  |  |  | checkbox in cell H33 as appropriate.
Click on the Help button for an explanation of this checkbox.
Max allow interior temp | 104
Max exterior temp | 114
Differential air temp (DT) | 10 | deg F
DT with solar contribution |  | deg F
Internally generator losses | .05 | kW
| Surface | Insulation | Steel | Steel | Total eq. | Heat xfer | Enclosure |  | a - Solar
q=(ADT)/R | Area | R value | thickness | R value | R value1 | (q) BTU/hr | surf. Temp. | Surface Color | Absorption
roof | 5.8333 | 2 | 0.123 | 0.00039122 | 2.6704 | 19.4173 | 112.8889 |  | 0
front | 20.4167 | 0 | 0.123 | 0.00039122 | 0.67039 | 270.7098 | 112.8889 |  | 0
left side | 9.7222 | 0 | 0.123 | 0.00039122 | 0.67039 | 128.9094 | 112.8889 |  | 0
right side | 9.7222 | 0 | 0.123 | 0.00039122 | 0.67039 | 128.9094 | 112.8889 |  | 0
back | 20.4167 | 0 | 0.123 | 0.00039122 | 0.67039 | 270.7098 | 112.8889 |  | 0
| 66.1111 | sq. ft |  |  |  | 989.2558 | BTU/hr loss
1 includes inside air film and paint heat transfer resistance of R 0.67 | [5 empty] | 0.28993 | kW
Ave solar rad/day (40 deg lat) | 2325 | (BTU/day/ft2)
Ave solar rad/hr (40 deg lat.)3 | 96.875 | (BTU/hr/ft2) |  | 290.625 | (BTU/hr/ft2) peak
Peak/Ave solar radiation2 | 3
Actual latitude | 40 | deg |  | 290.6249 | (BTU/hr/ft2) adjusted peak
Hour of Day | 14 | (12:noon, 0 or 24:midnight) |  |  | 1 | roof
[5 empty] | 0.28402 | front
2 Ratio decreases to 1 winter and increases to 3 in summer |  |  |  |  | 0 | left |  | q4 = 2DK4 (TW - T3) | ground heat loss
3From www.agcom.purdue.edu/AgCom/Pubs/AE/AE-88.html |  |  |  |  | 0.43388 | right |  | K = thermal conductivity | 314.4 | mild steel
[5 empty] | 0 | back |  | Allow reflections? | 0.5 | 0.5
[11 empty] | Gauge | Inches
Worst Case Calculations |  |  |  |  | color: | black | (all solar energy absorbed) |  |  |  | 10 | 0.138
absorption of surface for solar radiation |  |  |  |  | a | 0.9 | <unitless> |  |  |  | 11 | 0.123
radiation incident to surface (roof) |  |  |  |  | I | 290.6249 | BTU/hr ft2 |  |  |  | 12 | 0.108
coefficient of heat transmission of surface |  |  |  |  | U | 0.5 | BTU/hr ft2 OF |  |  |  | 13 | 0.093
interior temperature of enclosure |  |  |  |  | ti | 104 | OF |  |  |  | 14 | 0.079
exterior ambient temperature |  |  |  |  | to | 114 | OF |  |  |  | 15 | 0.071
coefficient of heat transmission by convection (function of wind speed) |  |  |  |  | ho | 4 | BTU/hr ft2 OF |  |  |  | 16 | 0.064
emittance of surface (ability to reject heat by radiation) |  |  |  |  | e | 0.9 | <unitless> |  |  |  | 17 | 0.058
net infrared radiation back to ambient |  |  |  |  | DR | 0 | BTU/hr ft2 |  |  |  | 18 | 0.052
[11 empty] | 19 | 0.046
|  |  |  | temperature of surface | ts | 171.0139 | OF | (worst case surface temperature rise) |  |  | 20 | 0.04
[11 empty] | 21 | 0.037
H
W
D
Rr
Rf
Rs
Rb

## Solar Day
| Roof |  | Front | Left Side | Right Side | Back
Hour | Watts | Normalized | Normalized | Normalized | Normalized | Normalized | Peak: | 1750
0 | 0 | 0% | 0% | 0% | 0% | 0%
1 | 0 | 0% | 0% | 0% | 0% | 0%
2 | 0 | 0% | 0% | 0% | 0% | 0%
3 | 0 | 0% | 0% | 0% | 0% | 0%
4 | 0 | 0% | 0% | 0% | 0% | 0%
5 | 0 | 0% | 0% | 0% | 0% | 0%
6 | 500 | 28.57% | 8.115% | 27.86% | 0% | 0%
7 | 1000 | 57.14% | 16.23% | 51.48% | 0% | 0%
8 | 1500 | 85.71% | 24.34% | 67.01% | 0% | 0%
9 | 1700 | 97.14% | 27.59% | 60.57% | 0% | 0%
10 | 1750 | 100% | 28.4% | 43.39% | 0% | 0%
11 | 1710 | 97.71% | 27.75% | 21.74% | 0% | 0%
12 | 1700 | 97.14% | 27.59% | 0% | 0% | 0%
13 | 1710 | 97.71% | 27.75% | 0% | 21.74% | 0%
14 | 1750 | 100% | 28.4% | 0% | 43.39% | 0%
15 | 1750 | 100% | 28.4% | 0% | 62.35% | 0%
16 | 1650 | 94.29% | 26.78% | 0% | 73.72% | 0%
17 | 800 | 45.71% | 12.98% | 0% | 41.19% | 0%
18 | 500 | 28.57% | 8.115% | 0% | 27.86% | 0%
19 | 0 | 0% | 0% | 0% | 0% | 0%
20 | 0 | 0% | 0% | 0% | 0% | 0%
21 | 0 | 0% | 0% | 0% | 0% | 0%
22 | 0 | 0% | 0% | 0% | 0% | 0%
23 | 0 | 0% | 0% | 0% | 0% | 0%
24 | 0 | 0% | 0% | 0% | 0% | 0%
Assume 'front' (largest face) faces south. As a result, even if this enclosure were stand-alone, the back surface
would not receive any solar radiation during the longest day of the year.